**WALL-MOUNTED CABINET TECHNICAL SPECIFICATION**

1. **GENERAL CONDITIONS**

19” wall-mounted rack cabinet must have ISO 9001: 2015 quality management system certificate and TSE certificate including the standards of EN 61587-1, IEC 60917, IEC 60297. Brand of the product, commercial title, height, width and depth information must be placed on the TSE document.

1. **DIMENSIONS**

Complies with IEC 60297 standard. 19” cabinets must be 5U (2U vertical+3U horizontal) height, 500 mm. width and 140 mm. depth.

1. **LOAD CARRYING CAPACITY**

Must be 80 kg.

1. **BOTTOM CHASIS**

The bottom chasis must have a monobloc twisted and welded structure.

1. **FRONT COVER**

The front cover can be opened with a mechanical stop and locked with "O" type lock unit. Plexiglass area must be available.

1. **19” UPRIGHTS AND SIDE ARMS**

The 19 "device mounting capacity must be 5U (2U vertical + 3U horizontal) in total.

1. **COLOR**

It must be black (RAL 9005) or light grey (RAL 7035) as standard.

1. **DOCUMENTARY MATERIALS USED IN CABINET MANUFACTURING**

**Sheet Steel:** EN 10346: 20015 DX51D+Z, EN 10130: 2006 DC01

**Electrostatic Powder Coating:** ISO6860, ISO2409, ISO1520, ISO2815, ISO6272, ISO7253 ISO6270-1, ISO2812**,** ISO 9001, RoHS

**Lock:** IEC 62474, REACH, RoHS

**Fan:** IEC 60335-2-80:2002, IEC 60335-1:2010

1. **TESTS AND CERTIFICATES**

**Resistance to environmental conditions and corrosion;**

**Stability, mechanical safety, resistance to static, dynamic and mechanical loads;**

**Resistance to vibration, mechanical shock and impact;**

**Degrees of mechanical protection provided by the enclosure (IP20);**

**Electrical grounding continuity;**

**Fire and flame resistance;**

Have been tested according to the standard “EN 61587-1” with the normative standards: IEC 60917, IEC 60297, IEC 60068-1, IEC 60068-2, IEC 60695-11-10, IEC 60950-1 contained and certified by the notified organizations.

**TSE Certificate No:**003788-TSE-08/02

**EAC** **Certificate No:** 0443637, 0776963, 0345864, 0401678, 0776653

**Corrosion:** ISO 9227 standard complied by the test report METALTEK AB-0547-T / 0157-1

**Transport:** ETS 300 019-1-2 Class 2.3 comply with internal testing

**Storage:** ETS 300 019-1-1 Class 1.2 comply with internal testing

**Surface Finish:** Electrostatic powder coated c/with surface treatment, 80+/-5 micron paint thickness